## PlantCharacteristics
Plant Characteristics
Total Plant Thermal Power (MWt) | 3400
Net Electrical Power (MWe) | 1117
Number of Reactors | 1
Number of turbines | 1
Thermal Efficiency | 32.85%
Heat Rejected (MWt) | 2283
# Fuel Assemblies | 193
Safety | Passive
Gen III+ or later | TRUE
Construction duration (months) | 52
Integral PWR | FALSE
RPV diameter (m) | 4.5
RPV thickness (m) | 0.2
FOAK construction duration (months) | 68
NOAK construction duration (months) | 47

## Learning
Account | Initial unit number

## Modules
Account | Percent Offsite Work | Offsite Efficiency | Factory Cost (2018 USD)
Note on D1: William Stewart: This is the cost to build the factory that will create the modules

## 21-Structures&Improvements
|  |  | Detailed Inputs | [13 empty] | Direct Cost Input
Account | Name | Method | Shape | Inside? | Portions | Dimensions (meters) | Foundation thickness (meters) | Superstructure type | Superstructure thickness (meters) | Rebar density | Interior concrete method | Interior concrete | SSCs moved to | Seismic Class 1 | Steel plate composite | High strength rebar | Direct cost per RX (2018 USD) | Reference EEDB Cost (1987 USD)
A.212. | Reactor Building | Detailed (EEDB based) | Cylinder w/ dome | None | 1 | [44.2, 45.7, 0] | 3 | Reinforced concrete | 1 | Default | Building volume | - |  | TRUE | Two sided | FALSE
A.212.15 | Containment Liner | Detailed (EEDB based) | Cylinder w/ dome | None | 1 | [44.2, 45.7, 0] | 0.01 | Standalone steel building | 0.01 | Default | Building volume | - |  | TRUE | FALSE | FALSE
A.219. | Reactor Shield Building | Detailed (EEDB based) | Cylinder w/ dome | None | 1 | [0,0,0] | 0 | Reinforced concrete | 0 | Default | Building volume | - |  | TRUE | FALSE | FALSE
A.213. | Turbine Room & Heater Bay | Detailed (EEDB based) | Rectangular | None | 1 | [47, 88, 47] | 0.3 | Steel frame | 0.3 | Default | Building volume | - |  | FALSE | FALSE | FALSE
A.214. | Security Building | Fixed cost | - | None | 1 | [-] | - | - |  | Default | - | - |  | - | FALSE | FALSE
A.215. | Aux Building & RHR Equipment Vault | Detailed (EEDB based) | Rectangular | None | 1 | [37, 19, 19] | 1.2 | Reinforced concrete | 0.6 | Default | Building volume | - |  | TRUE | FALSE | FALSE
A.216. | Waste Process Building & Tank Farm | Detailed (EEDB based) | Rectangular | None | 1 | [54, 24, 13] | 1.2 | Reinforced concrete | 0.6 | Default | Building volume | - |  | TRUE | FALSE | FALSE
A.217. | Fuel Storage Building | Detailed (EEDB based) | Rectangular | None | 1 | [28, 25, 27] | 0.6 | Reinforced concrete | 0.3 | Default | Building volume | - |  | TRUE | FALSE | FALSE
A.218A. | Control Room & DG Building | Detailed (EEDB based) | Rectangular | None | 1 | [20, 19, 7] | 0.6 | Reinforced concrete | 0.3 | Default | Building volume | - |  | FALSE | FALSE | FALSE
A.218B. | Admin Building | Detailed (EEDB based) | Rectangular | None | 1 | [0,0,0] | 0.3 | Steel frame | 0.3 | Default | Building volume | - | A.218A. | FALSE | FALSE | FALSE
A.218D. | Fire Pump House | Fixed cost | - | None | 1 | [-] | - | - | - | Default | - | - |  | - | FALSE | FALSE
A.218E. | Emergency Feedwater Pump Building | Detailed (EEDB based) | Rectangular | None | 1 | [0, 0, 0] | 1.2 | Reinforced concrete | 0.6 | Default | Building volume | - | A.215. | TRUE | FALSE | FALSE
A.218F. | Radiological Access Tunnel | Plant power scaling | - | None | 1 | [-] | - | - | - | Default | - | - |  | - | FALSE | FALSE
A.218G. | Electrical Tunnel | Detailed (EEDB based) | Rectangular | None | 1 | [0, 0, 0] | 1.2 | Reinforced concrete | 0.6 | Default | Building volume | - | A.215. | TRUE | FALSE | FALSE
A.218H. | Non-essential Switchgear Building | Detailed (EEDB based) | Rectangular | None | 1 | [0, 0, 0] | 0.3 | Steel frame | 0.3 | Default | Building volume | - | A.215. | FALSE | FALSE | FALSE
A.218J. | Main Steam & Feedwater Pipe Enclosure 1 & 2 | Detailed (EEDB based) | Rectangular | None | 1 | [0, 0, 0] | 1.2 | Reinforced concrete | 0.6 | Default | Building volume | - | A.215. | TRUE | FALSE | FALSE
A.218K. | Pipe Tunnels | Plant power scaling | - | None | 1 | [-] | - | - | - | Default | - | - |  | - | FALSE | FALSE
A.218L. | Technical Support Center | Fixed cost | - | None | 1 | [-] | - | - | - | Default | - | - |  | - | FALSE | FALSE
A.218P. | Containment Hatch Missile Shield | Detailed (EEDB based) | Rectangular | None | 1 | [0, 0, 0] | 1.2 | Reinforced concrete | 0.6 | Default | Building volume | - | A.212. | TRUE | FALSE | FALSE
A.218S. | Waste Water Treatment Building | Detailed (EEDB based) | Rectangular | None | 1 | [0, 0, 0] | 0.3 | Steel frame | 0.3 | Default | Building volume | - | A.216. | FALSE | FALSE | FALSE
A.218T. | Ultimate Heat Sink Structure | Detailed (EEDB based) | Rectangular | None | 1 | [0, 0, 0] | 0.3 | Steel frame | 0.3 | Default | Building volume | - | A.215. | FALSE | FALSE | FALSE
A.218V. | Control Room Air Intake Structure | Fixed cost | - | None | 1 | [3, 3, 2] | 0.9 | - | 0.6 | Default | - | - |  | - | FALSE | FALSE
Note on E2: William Stewart: If this structure is wholly contained in another structure indicate it here
Note on G2: William Stewart: Cylinder w/ dome: [diameter, height, 0] Cylinder: [diameter, height, 0] Rectangular: [length, width, height] Liner [-]
Note on K2: W. Robb Stewart: [Substructure, superstructure, interior concrete] Interior cocnrete only matters for reactor building. "Default" assumes the default values from EEDB. Containment: [0.047, 0.049, 0.039] Turbine building: [0.011, 0.013] (interior concrete included in superstructure) Auxiliary building: [0.019, 0.022] (interior concrete included in superstructure)
Note on M2: William Stewart: Building volume: Empty Superstructure mult: [Scaler (interior walls as fraction of exterior walls), number of floors] Volume: Cubic meters
Note on N2: W. Robb Stewart: If a building does not exist in a plant design, indicate what other building the associated SSCs were moved to

## 22-ReactorEquipment
|  |  |  | Detailed Inputs |  |  | Direct Cost Input
Account | Category | Name | Method | Parameter (s) | Count per plant (DI) | Value | Direct cost per RX (2018 USD) | Count per plant (DCI) | Reference EEDB Cost (1987 USD)
A.221.1 | Reactor equipment | RPV | Detailed (CE) | Vessel mass (kg) | 1 | 352000 |  |  | 70290399
A.221.3 | Reactor equipment | RPV Internals | Detailed | RPV diameter (m) | 1 | 4.5
A.221.2 | Reactor equipment | Control rods | Detailed | Number of CRs per RX | 1 | 69 |  |  | 56511634
A.222.11 | Main heat transport system | Primary coolant pump | Detailed (CE) | Power (kW) (m3/sec*head*specific weight) | 4 | 5000 |  |  | 46653127
A.222.12 | Main heat transport system | Primary system piping | Detailed | Primary system piping mass (kg) | 1 | 77000 |  |  | 9901444
A.222.13 | Main heat transport system | Steam generators | Detailed (CE) | HT surface area (m2) | 2 | 11477 |  |  | 53034613
A.222.14 | Main heat transport system | Pressurizer | Detailed (CE) | Pressurizer mass (kg) | 1 | 106000 |  |  | 3650698
A.223.1 | Safeguards system | Residual heat removal | RX power scaling | [5 empty] | 5247201
A.223.3 | Safeguards system | Safety injection system | RX power scaling | [5 empty] | 9919243
A.223.4 | Safeguards system | Containment spray | Detailed | Containment volume (m3) | 1 | 86163.9381 |  |  | 5301297
A.223.5 | Safeguards system | Combustible gas control | Detailed | Containment volume (m3) | 1 | 86163.9381 |  |  | 1080923
A.224.1 | Radwaste processing | Liquid waste system | Detailed | Primary flow rate (liters/sec) | 1 | 19880 |  |  | 11383735
A.224.2 | Radwaste processing | Rad gas waste processing | Detailed | Primary flow rate (liters/sec) | 1 | 19880 |  |  | 1526383
A.224.3 | Radwaste processing | Solid waste system | Plant power scaling | [5 empty] | 8032289
A.225.111 | Fuel handling and storage | Fuel crane | Detailed (CE) | Fuel crane capacity (tons) | 1 | 2 |  |  | 1552247
A.225.112 | Fuel handling and storage | Monorails/hoists | Fixed cost
A.225.113 | Fuel handling and storage | Fuel elevator | Fixed cost
A.225.114 | Fuel handling and storage | Spent fuel cask crane | Detailed (CE) | Fuel cask capacity | 1 | 113
A.225.12 | Fuel handling and storage | Fuel handling tools | Fixed cost
A.225.13 | Fuel handling and storage | Transfer system | Fixed cost
A.225.3 | Fuel handling and storage | Service platforms | Fixed cost | [5 empty] | 135892
A.225.4 | Fuel handling and storage | Fuel storage, cleaning, inspection | Detailed | Spent fuel pool volume (m3) | 1 | 750 |  |  | 2492958
A.217.3 | Fuel Storage Building | Spent fuel pool liner | Detailed pool | Spent fuel pool surface area (m2) | 1 | 480 |  |  | 3513900
A.212.3 | Reactor Building | Passive cooling pool liner | Detailed pool | Passive cooling pool surface area (m2) | 1 | 1000
A.226.1 | Other equipment | Intert gas system | Fixed cost | [5 empty] | 1240051
A.226.3 | Other equipment | Reactor makeup water system | Fixed cost | [5 empty] | 1492582
A.226.4 | Other equipment | Coolant treatment and recycle | Detailed | Primary flow rate (liters/sec) | 1 | 19880 |  |  | 17186529
A.226.6 | Other equipment | Fluid leak detection system | Fixed cost | [5 empty] | 173004
A.226.71 | Other equipment | Nuclear service water system | Detailed | RX power (MW) | 1 | 3400 |  |  | 11187252
A.226.72 | Other equipment | Primary component cooling water | Detailed | Primary flow rate (liters/sec) | 1 | 19880 |  |  | 8184572
A.226.8 | Other equipment | Maintenance equipment | Fixed cost | [5 empty] | 4374197
A.226.9 | Other equipment | Sampling equipment | Fixed cost
A.227.11 | Reactor I&C | NSS Control Board | Detailed | Number of RXs | 1 | 1 |  |  | 3603548
A.227.15 | Reactor I&C | HVAC Panels | Fixed cost
A.227.16 | Reactor I&C | Radwaste Panels & Racks | Fixed cost
A.227.17 | Reactor I&C | Local Panels & Cabinets | Fixed cost
A.227.18 | Reactor I&C | Instrument Ranks | Fixed cost
A.227.19 | Reactor I&C | Alarm System | Detailed | Number of CRs per RX | 1 | 69
A.227.2 | Reactor I&C | Process Computer | Detailed | Number of RXs | 1 | 1 |  |  | 3253606
A.227.3 | Reactor I&C | Monitoring Systems | Fixed cost | [5 empty] | 4006562
A.227.4 | Reactor I&C | Plant Control Systems | Detailed | Number of CRs per RX | 1 | 69 |  |  | 3183570
A.227.5 | Reactor I&C | Reactor Plant I&C Tubing & Fitting | Detailed | Number of CRs per RX | 1 | 69 |  |  | 3902000
A.227.9 | Reactor I&C | TMI Instrumentation | Detailed | Number of CRs per RX | 1 | 69 |  |  | 3605984
A.228.1 | Reactor Plant Miscellaneous Items | Field Painting | Fixed cost | [5 empty] | 755364.7879
A.228.2 | Reactor Plant Miscellaneous Items | Qualification of Welders | Fixed cost | [5 empty] | 3133664.3689
A.228.4 | Reactor Plant Miscellaneous Items | Reactor Plant Insulation | Detailed | RPV insulated area (m2) | 1 | 250 |  |  | 3563245.8432
A.229.1 | NuScale Equipment | Containment vacuum pump | Detailed | Pump power (kW) | 1 | 0
A.229.2 | NuScale Equipment | Containment flooding & drain | Detailed | Evacuated volume (m3) | 1 | 0
A.229.3 | HTGR Equipment | Reactor Cavity Cooling System | Direct cost input | RPV surface area (m2) | 1 | 150.7964 | 0 | 1
A.229.4 | HTGR Equipment | Refueling Equipment | Direct cost input | Core diameter (m) | 1 | 4 | 0 | 1
A.229.5 | HTGR Equipment | He Purification Equipment | Direct cost input | He purif flow rate (kg/s) | 1 | 0.88 | 0 | 1
A.229.6 | HTGR Equipment | He Circulator | Direct cost input | Circulator power (kW) | 1 | 2791 | 0 | 1
A.229.7 | BWR | Isolation Condensers | Direct cost input | Thermal power rating (MW) | 4 | 30 | 0 | 1
Note on G31: William Stewart: TO DO: 226.71 and 226.72 both include additional BV scalers

## 23-TurbineEquipment
|  |  |  | Detailed Inputs |  |  | Direct Cost Input |  | Power scaling
Account | Category | Name | Method | Parameter (s) | Count per plant (DI) | Value | Direct cost per RX (2018 USD) | Count per plant (DCI) | Count per plant | Reference EEDB Cost (1987 USD)
A.231. | Turbine Equipment | Turbine Generator | Plant electric power scaling |  |  |  |  | 1 | 1 | 133984273
A.233. | Turbine Equipment | Condensing System | Plant electric power scaling |  |  |  |  | 1 | 1 | 28981986
A.234. | Turbine Equipment | Feedwater Heating System | Plant electric power scaling | HT Surface Area (m2) | 1 | 79440.7713 |  | 1 | 1 | 23588801
A.235. | Turbine Equipment | Other Turbine Plant Equipment | Plant electric power scaling |  |  |  |  | 1 | 1 | 22323194
A.236. | Turbine Equipment | Instrumentation & Control | Plant electric power scaling |  |  |  |  | 1 | 1 | 6854212
A.237. | Turbine Equipment | Turbine Plant Misc. Items | Plant electric power scaling |  |  |  |  | 1 | 1 | 8045900

## 24-ElectricalEquipment
|  |  |  | Detailed Inputs |  |  | Direct Cost Input |  | Power scaling
Account | Category | Name | Method | Parameter (s) | Count per plant (DI) | Value | Direct cost per RX (2018 USD) | Count per plant (DCI) | Count per plant | Reference EEDB Cost (1987 USD)
A.241. | Electrical Equipment | Switchgear | Plant electric power scaling | Safety | 1 | Passive |  |  | 1 | 11946283
A.242. | Electrical Equipment | Station Service Equipment | Plant electric power scaling | Safety | 1 | Passive |  |  | 1 | 20163388
A.243. | Electrical Equipment | Switchboards | Plant electric power scaling | Safety | 1 | Passive |  |  | 1 | 2048898
A.244. | Electrical Equipment | Protective Equipment | Plant electric power scaling | Safety | 1 | Passive |  |  | 1 | 4261386
A.245. | Electrical Equipment | Electrical Structure & Wiring Container | Plant electric power scaling | Safety | 1 | Passive |  |  | 1 | 22301683
A.246. | Electrical Equipment | Power & Control Wiring | Plant electric power scaling | Safety | 1 | Passive |  |  | 1 | 20601086

## 25-MiscEquipment
|  |  |  | Detailed Inputs |  |  | Direct Cost Input
Account | Category | Name | Method | Parameter (s) | Count per plant (DI) | Value | Direct cost per RX (2018 USD) | Count per plant (DCI) | Reference EEDB Cost (1987 USD)
A.251.111 | Transportation and lift equipment | TG Crane | RX power scaling | TG crane capacity | 1 | 190 |  |  | 1433136
A.251.112 | Transportation and lift equipment | HB crane | RX power scaling | Heater bay crane capacity | 1 | 90 |  |  | 575934
A.251.12 | Transportation and lift equipment | Containment crane | RX power scaling | Containment crane | 1 | 380 |  |  | 3000136
A.251.16 | Transportation and lift equipment | Misc. cranes | Fixed cost | [5 empty] | 519581
A.251.17 | Transportation and lift equipment | DG crane | RX power scaling | Diesel building crane | 2 | 4.5 |  |  | 465043
A.252.1 | Air, water, and steam service system | Air system | Detailed volume | Volume of 212, 213, 215, 216, 217 |  |  |  |  | 5725138
A.252.2 | Air, water, and steam service system | Water system | Detailed volume | Volume of 212, 213, 215, 216, 217 |  |  |  |  | 18534959
A.252.3 | Air, water, and steam service system | Steam system | Detailed volume | Volume of 212, 213, 215, 216, 217 |  |  |  |  | 4277339
A.252.4 | Air, water, and steam service system | Plant fuel oil system | Fixed cost | [5 empty] | 188218
A.253. | Communications equipment | Communications equipment | Detailed volume | Volume of 212, 213, 215, 216, 217 |  |  |  |  | 6415046
A.254. | Furnishings and fixtures | Furnishings and fixtures | Detailed volume | Volume of 212, 213, 215, 216, 217 |  |  |  |  | 2735984
A.255. | Waste water treatment | Waste water treatment | Fixed cost | [5 empty] | 2831384

## 26-HeatRejectionSystem
|  |  |  | Detailed Inputs |  |  | Direct Cost Input |  | Power scaling
Account | Category | Name | Method | Parameter (s) | Count per plant (DI) | Value | Direct cost per RX (2018 USD) | Count per plant (DCI) | Count per plant | Reference EEDB Cost (1987 USD)
A.211.1 | Structures & Improvments | General Yardwork | Detailed | Site area (acres) | 1 | 23 |  |  | 1 | 1020353
A.211.4 | Structures & Improvments | Railroads | Plant power scaling | Length of new railroad (meters) | 1 | 9500 |  |  | 1 | 1020353
A.211.7111 | Structures & Improvments | Dewatering | Plant power scaling | Sum of excavation (m3) | 1 | 296000 |  |  | 1
A.211.7112 | Structures & Improvments | Earth Excavation | Plant power scaling | Volume of earth excavation (m3) | 1 | 92000 |  |  | 1
A.211.7113 | Structures & Improvments | Rock Excavation | Plant power scaling | Volume of rock excavation (m3) | 1 | 150000 |  |  | 1
A.211.7114 | Structures & Improvments | Excavation - Trench | Plant power scaling | Volume of trench excavation (m3) | 1 | 54000 |  |  | 1
A.211.712 | Structures & Improvments | Fill & Backfill | Detailed volume | Volume of 212, 213, 215, 216, 217 |  |  |  |  | 1
A.261.1 | Heat rejection system | Makeup Water Intake Building | Detailed | Rejected thermal power (MW) | 1 | 2283 |  |  | 1 | 1020353
A.261.2 | Heat rejection system | Circulation Water Pump House | Detailed | Rejected thermal power (MW) | 1 | 2283 |  |  | 1 | 2092104
A.261.3 | Heat rejection system | Makeup Water Pretreatment Building | Detailed | Rejected thermal power (MW) | 1 | 2283 |  |  | 1 | 1220263
A.262.11 | Heat Rejection System | Water Intake Equipment | Detailed | Rejected thermal power (MW) | 1 | 2283 |  |  | 1 | 463845
A.262.12 | Heat Rejection System | Circulating Water System | Detailed | T/B Bldg - Cooling source distance (m) | 1 | 250 |  |  | 1 | 13949276
A.262.13 | Heat Rejection System | Cooling Towers | Detailed | Rejected thermal power (MW) | 1 | 2283 |  |  | 1 | 28782934
A.262.14 | Heat Rejection System | Cooling Tower Basins | Detailed | Rejected thermal power (MW) | 1 | 2283 |  |  | 1 | 81798
A.262.15 | Heat Rejection System | Main Cooling Tower Makeup & Blowdown System | Detailed | Rejected thermal power (MW) | 1 | 2283 |  |  | 1 | 1370392