## input_scaling
Header | Description | Account | Option 0 | Option 0 Formula | Option 1 | EEDB Base Unit Value 1 | Option 1 Exponent | Option 2 | EEDB Base Unit Value 2 | Option 2 Exponent | Option 3 | EEDB Base Unit Value 3 | Option 4 | EEDB Base Unit Value 4 | Option 4 Exponent | Concrete (CY) | Concrete Fill (CY) | Reinforcing steel (TN) | Structural steel (TN) | Embedded steel (TN) | Excavation (CY) | Wire & cable (LF) | NN Piping (LB) | SC Piping (LB)
Yardwork | General Yardwork | A.211.1 |  |  | Area | 62 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 19732168 | Fixed cost | 1 | 1 | 170 |  | 83
Yardwork | Railroads | A.211.4 |  |  | Railroad length | 9500 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 8716768 | Fixed cost | 1 | 1
Yardwork | Dewatering | A.211.7111 |  |  | Excavation volume | 296000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 4119742.598 | Fixed cost | 1 | 1
Yardwork | Earth Excavation | A.211.7112 |  |  | Excavation volume | 92000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1366041.348 | Fixed cost | 1 | 1
Yardwork | Rock Excavation | A.211.7113 |  |  | Excavation volume | 150000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 12778367.8 | Fixed cost | 1 | 1
Yardwork | Excavation - Trench | A.211.7114 |  |  | Excavation volume | 54000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1302044.566 | Fixed cost | 1 | 1
Yardwork | Fill & Backfill | A.211.712 |  |  | Volume of 212, 213, 215, 216, 217 | 416524 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 29048792.94 | Fixed cost | 1 | 1 |  | 71000
Reactor building | Substructure | A.212.13 |  |  | Substructure volume | 4603 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 19193665 | Fixed cost | 1 | 1 | 8400 |  | 2700 |  | 3
Reactor building | Interior concrete | A.212.140 |  |  | Building volume | 92268 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 61879944 | Fixed cost | 1 | 1 | 8000 |  | 2100 |  | 360
Reactor building | Superstructure concrete | A.212.141 |  |  | Superstructure volume | 11248 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 53362385 | Fixed cost | 1 | 1 | 13050 |  | 4250 |  | 20
Reactor building | Structural & Misc steel | A.212.142 |  |  | Building volume | 92268 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 6727151 | Fixed cost | 1 | 1 |  |  |  | 410
Reactor building | Painting | A.212.149 |  |  | Superstructure area | 9373 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 15007922 | Fixed cost | 1 | 1
Reactor building | Containment liner | A.212.15 | Containment vessel | [13128, 38, Pressure vessel - exponent, RPV - nuclear escalation] | Superstructure area | 9373 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 60848829 | Fixed cost | 1 | 1
Reactor building | Plumbing & Drains | A.212.21 |  |  | Building volume | 92268 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1404249 | Fixed cost | 1 | 1 | [7 empty] | 23000
Reactor building | HVAC | A.212.22 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 316069 | Fixed cost | 1 | 1
Reactor building | Safety HVAC | A.212.23 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 5917967 | Fixed cost | 1 | 1
Reactor building | Lighting & Service power | A.212.24 |  |  | Building volume | 92268 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 4808686 | Fixed cost | 1 | 1
Reactor building | Elevator | A.212.25 |  |  | Constant | 1 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 319651 | Fixed cost | 1 | 1
Reactor building | Passive cooling pool | A.212.3 | Surface area | [Pool surface area cost] | [6 empty] | Direct cost | 1
Reactor shield building | Superstructure concrete | A.219.141 |  |  | Superstructure volume | 11248 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 53362385 | Fixed cost | 1 | 1 | 13050 |  | 4250 |  | 20
Reactor shield building | Structural & Misc steel | A.219.142 |  |  | Building volume | 92268 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 6727151 | Fixed cost | 1 | 1 |  |  |  | 410
Reactor shield building | Painting | A.219.149 |  |  | Superstructure area | 9373 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 15007922 | Fixed cost | 1 | 1
Turbine generator building | Substructure | A.213.13 |  |  | Substructure volume | 1830 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 21213032 | Fixed cost | 1 | 1 | 12800 |  | 910 |  | 100
Turbine generator building | Superstructure concrete | A.213.141 |  |  | Superstructure volume | 5112 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2275593 | Fixed cost | 1 | 1 | 800 |  | 70 |  | 10
Turbine generator building | Structural & Misc steel | A.213.142 |  |  | Building volume | 212000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 39924296 | Fixed cost | 1 | 1 |  |  |  | 3900
Turbine generator building | Exterior walls | A.213.143 |  |  | Superstructure area | 17040 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 4557780 | Fixed cost | 1 | 1
Turbine generator building | Roofing | A.213.144 |  |  | Substructure area | 6100 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1817917 | Fixed cost | 1 | 1 | 800 |  | 38
Turbine generator building | Roofing | A.213.145 |  |  | Substructure area | 6100 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 911815 | Fixed cost | 1 | 1
Turbine generator building | Interior walls | A.213.146 |  |  | Building volume | 212000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 728082 | Fixed cost | 1 | 1
Turbine generator building | Doors/windows | A.213.147 |  |  | Building volume | 212000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1629229 | Fixed cost | 1 | 1
Turbine generator building | Painting | A.213.149 |  |  | Superstructure area | 17040 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2327752 | Fixed cost | 1 | 1
Turbine generator building | Plumbing & Drains | A.213.21 |  |  | Building volume | 212000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 4827375 | Fixed cost | 1 | 1 | [7 empty] | 25980
Turbine generator building | HVAC | A.213.22 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 3208022 | Fixed cost | 1 | 1
Turbine generator building | Lighting & Service power | A.213.24 |  |  | Building volume | 212000 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2025741 | Fixed cost | 1 | 1
Turbine generator building | Elevator | A.213.25 |  |  | Constant | 1 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 335696 | Fixed cost | 1 | 1
Security building | Security building | A.214. | [5 empty] | RX power | 3417 | Structures - plant power costs | Direct cost | 4533007 | Fixed cost | 1 | 1 | 975 |  | 78 | 60 | 2
Primary aux building | Substructure | A.215.13 |  |  | Substructure volume | 1553 | Structures - unit costs |  |  |  | Direct cost | 2549377 | Fixed cost | 1 | 1 | 2100 |  | 260 |  | 7
Primary aux building | Superstructure concrete | A.215.141 |  |  | Superstructure volume | 3326 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 35505158 | Fixed cost | 1 | 1 | 11800 |  | 1700 |  | 130
Primary aux building | Structural & Misc steel | A.215.142 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 4797799 | Fixed cost | 1 | 1 |  |  |  | 450
Primary aux building | Roofing | A.215.145 |  |  | Substructure area | 1294 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 147964 | Fixed cost | 1 | 1
Primary aux building | Interior walls | A.215.146 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 457789 | Fixed cost | 1 | 1
Primary aux building | Doors/windows | A.215.147 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 169898 | Fixed cost | 1 | 1
Primary aux building | Painting | A.215.149 |  |  | Superstructure area | 5544 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 825071 | Fixed cost | 1 | 1
Primary aux building | Plumbing & Drains | A.215.21 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1892676 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC - Safety HVAC - Rotating Machinery | A.215.221 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2897193 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC - Heat Transfer Equipment | A.215.222 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2295632 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC - Tanks & Pressure Vessels | A.215.223 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 72147 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC - Purification & Filtration Equipment | A.215.224 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 569667 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC - Piping & Ductwork | A.215.225 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 6722979 | Fixed cost | 1 | 1 | [7 empty] | 88745
Primary aux building | Safety HVAC - Valves & Dampers | A.215.226 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 397242 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC - Piping & Miscellaneous Items | A.215.227 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 216645 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC - Instrumentation & Control | A.215.228 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 46688 | Fixed cost | 1 | 1
Primary aux building | Safety HVAC | A.215.23 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1303117 | Fixed cost | 1 | 1
Primary aux building | Lighting & Service power | A.215.24 |  |  | Building volume | 36232 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1791941 | Fixed cost | 1 | 1
Primary aux building | Elevator | A.215.25 |  |  | Constant | 1 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 490653 | Fixed cost | 1 | 1
Waste process building | Substructure | A.216.13 |  |  | Substructure volume | 2074 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 5316020 | Fixed cost | 1 | 1 | 6000 |  | 305 |  | 30
Waste process building | Superstructure concrete | A.216.141 |  |  | Superstructure volume | 4428 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 31164024 | Fixed cost | 1 | 1 | 8300 |  | 1200 |  | 160
Waste process building | Structural & Misc steel | A.216.142 |  |  | Building volume | 53328 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 5557784 | Fixed cost | 1 | 1 |  |  |  | 550
Waste process building | Exterior walls | A.216.143 |  |  | Superstructure area | 7380 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1072533 | Fixed cost | 1 | 1
Waste process building | Roofing | A.216.144 |  |  | Substructure area | 1728 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 602378 | Fixed cost | 1 | 1 | 370 |  | 20
Waste process building | Roofing | A.216.145 |  |  | Substructure area | 1728 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 275826 | Fixed cost | 1 | 1
Waste process building | Interior walls | A.216.146 |  |  | Building volume | 53328 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 8845 | Fixed cost | 1 | 1
Waste process building | Doors/windows | A.216.147 |  |  | Building volume | 53328 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 141403 | Fixed cost | 1 | 1
Waste process building | Finishing | A.216.148 |  |  | Building volume | 53328 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 11110 | Fixed cost | 1 | 1
Waste process building | Painting | A.216.149 |  |  | Superstructure area | 7380 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 651250 | Fixed cost | 1 | 1
Waste process building | Plumbing & Drains | A.216.21 |  |  | Building volume | 53328 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1527441 | Fixed cost | 1 | 1
Waste process building | HVAC | A.216.22 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 4360580 | Fixed cost | 1 | 1 | [7 empty] | 3240
Waste process building | Lighting & Service power | A.216.24 |  |  | Building volume | 53328 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1241924 | Fixed cost | 1 | 1
Waste process building | Elevator | A.216.25 |  |  | Constant | 1 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 547809 | Fixed cost | 1 | 1
Fuel storage building | Substructure | A.217.13 |  |  | Substructure volume | 1080 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1860398 | Fixed cost | 1 | 1 | 1800 |  | 160 |  | 5
Fuel storage building | Superstructure concrete | A.217.141 |  |  | Superstructure volume | 2304 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 11652567 | Fixed cost | 1 | 1 | 5000 |  | 500 |  | 50
Fuel storage building | Structural & Misc steel | A.217.142 |  |  | Building volume | 28800 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1527218 | Fixed cost | 1 | 1 |  |  |  | 160
Fuel storage building | Roofing | A.217.145 |  |  | Substructure area | 900 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 103576 | Fixed cost | 1 | 1
Fuel storage building | Doors/windows | A.217.147 |  |  | Building volume | 28800 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 57451 | Fixed cost | 1 | 1
Fuel storage building | Painting | A.217.149 |  |  | Superstructure area | 3840 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 160784 | Fixed cost | 1 | 1
Fuel storage building | Plumbing & Drains | A.217.21 |  |  | Building volume | 28800 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 510369 | Fixed cost | 1 | 1
Fuel storage building | HVAC | A.217.22 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1710011 | Fixed cost | 1 | 1 | [7 empty] | 2915
Fuel storage building | Safety HVAC | A.217.23 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2165644 | Fixed cost | 1 | 1
Fuel storage building | Lighting & Service power | A.217.24 |  |  | Building volume | 28800 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 402646 | Fixed cost | 1 | 1
Fuel storage building | Spent fuel pool liner | A.217.3 | Surface area | [Pool surface area cost] | Spent fuel pool surface area | 544 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 9718863 | Fixed cost | 1 | 1
CR/DG building | Substructure | A.218A.13 |  |  | Substructure volume | 2268 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2111291 | Fixed cost | 1 | 1 | 1050 |  | 170 |  | 9
CR/DG building | Superstructure concrete | A.218A.141 |  |  | Superstructure volume | 3755 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 37270294 | Fixed cost | 1 | 1 | 11800 |  | 1400 |  | 115
CR/DG building | Structural & Misc steel | A.218A.142 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 7760973 | Fixed cost | 1 | 1 |  |  |  | 770
CR/DG building | Roofing | A.218A.145 |  |  | Substructure area | 1890 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 288926 | Fixed cost | 1 | 1
CR/DG building | Interior walls | A.218A.146 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 4297607 | Fixed cost | 1 | 1
CR/DG building | Doors/windows | A.218A.147 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 191525 | Fixed cost | 1 | 1
CR/DG building | Finishing | A.218A.148 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 374571 | Fixed cost | 1 | 1
CR/DG building | Painting | A.218A.149 |  |  | Superstructure area | 6258 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 705656 | Fixed cost | 1 | 1
CR/DG building | Plumbing & Drains | A.218A.21 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 3018789 | Fixed cost | 1 | 1
CR/DG building | Safety HVAC - Safety HVAC - Rotating Machinery | A.218A.231 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1050899 | Fixed cost | 1 | 1
CR/DG building | Safety HVAC - Heat Transfer Equipment | A.218A.232 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1010402 | Fixed cost | 1 | 1
CR/DG building | Safety HVAC - Tanks & Pressure Vessels | A.218A.233 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 11830 | Fixed cost | 1 | 1
CR/DG building | Safety HVAC - Purification & Filtration Equipment | A.218A.234 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 274842 | Fixed cost | 1 | 1
CR/DG building | Safety HVAC - Piping & Ductwork | A.218A.235 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 9994692 | Fixed cost | 1 | 1 | [7 empty] | 14930 | 270000
CR/DG building | Safety HVAC - Valves & Dampers | A.218A.236 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 449760 | Fixed cost | 1 | 1
CR/DG building | Safety HVAC - Piping & Miscellaneous Items | A.218A.237 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 34666 | Fixed cost | 1 | 1
CR/DG building | Safety HVAC - Instrumentation & Control | A.218A.238 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 387888 | Fixed cost | 1 | 1
CR/DG building | Lighting & Service power | A.218A.24 |  |  | Building volume | 48762 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2645665 | Fixed cost | 1 | 1
Admin building | Substructure | A.218B.13 |  |  | Substructure volume | 1328 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2673937 | Fixed cost | 1 | 1 | 1700 |  | 135 |  | 6
Admin building | Superstructure concrete | A.218B.141 |  |  | Superstructure volume | 979 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1144519 | Fixed cost | 1 | 1 | 660 |  | 50 |  | 2
Admin building | Structural & Misc steel | A.218B.142 |  |  | Building volume | 53136 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 3307722 | Fixed cost | 1 | 1 |  |  |  | 390
Admin building | Exterior walls | A.218B.143 |  |  | Superstructure area | 3264 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 885876 | Fixed cost | 1 | 1
Admin building | Roofing | A.218B.144 |  |  | Substructure area | 4428 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1325710 | Fixed cost | 1 | 1 | 600 |  | 29
Admin building | Roofing | A.218B.145 |  |  | Substructure area | 4428 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 634400 | Fixed cost | 1 | 1
Admin building | Interior walls | A.218B.146 |  |  | Building volume | 53136 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2649859 | Fixed cost | 1 | 1
Admin building | Doors/windows | A.218B.147 |  |  | Building volume | 53136 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 733487 | Fixed cost | 1 | 1
Admin building | Finishing | A.218B.148 |  |  | Building volume | 53136 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 822670 | Fixed cost | 1 | 1
Admin building | Painting | A.218B.149 |  |  | Superstructure area | 3264 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 406450 | Fixed cost | 1 | 1
Admin building | Plumbing & Drains | A.218B.21 |  |  | Building volume | 53136 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1689998 | Fixed cost | 1 | 1
Admin building | HVAC | A.218B.22 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 5455457 | Fixed cost | 1 | 1 | [7 empty] | 70240
Admin building | Safety HVAC | A.218B.23 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 48666 | Fixed cost | 1 | 1
Admin building | Lighting & Service power | A.218B.24 |  |  | Building volume | 53136 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1349895 | Fixed cost | 1 | 1
Admin building | Elevator | A.218B.25 |  |  | Constant | 1 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 137701 | Fixed cost | 1 | 1
Fire pump house | Fire pump house | A.218D. | [5 empty] | RX power | 3417 | Structures - plant power costs | Direct cost | 1225821 | Fixed cost | 1 | 1 | 250 |  | 20 | 20 | 3
Emergency feedwater pump building | Substructure | A.218E.13 |  |  | Substructure volume | 288 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 942975 | Fixed cost | 1 | 1 | 450 |  | 90 |  | 6
Emergency feedwater pump building | Superstructure concrete | A.218E.141 |  |  | Superstructure volume | 245 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 5980222 | Fixed cost | 1 | 1 | 1850 |  | 260 |  | 30
Emergency feedwater pump building | Structural & Misc steel | A.218E.142 |  |  | Building volume | 1440 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 445606 | Fixed cost | 1 | 1 |  |  |  | 25
Emergency feedwater pump building | Exterior walls | A.218E.143 |  |  | Superstructure area | 408 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 51941 | Fixed cost | 1 | 1
Emergency feedwater pump building | Roofing | A.218E.145 |  |  | Substructure area | 240 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 35036 | Fixed cost | 1 | 1
Emergency feedwater pump building | Doors/windows | A.218E.147 |  |  | Building volume | 1440 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 25903 | Fixed cost | 1 | 1
Emergency feedwater pump building | Painting | A.218E.149 |  |  | Superstructure area | 408 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 50374 | Fixed cost | 1 | 1
Emergency feedwater pump building | Plumbing & Drains | A.218E.21 |  |  | Building volume | 1440 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 383628 | Fixed cost | 1 | 1
Emergency feedwater pump building | Safety HVAC | A.218E.23 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 163701 | Fixed cost | 1 | 1 | [7 empty] | 330
Emergency feedwater pump building | Lighting & Service power | A.218E.24 |  |  | Building volume | 1440 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 250708 | Fixed cost | 1 | 1
Radiological access tunnel | Radiological access tunnel | A.218F. | [5 empty] | RX power | 3417 | Structures - plant power costs | Direct cost | 2632082 | Fixed cost | 1 | 1 | 930 |  | 110 | 10 | 6
Electrical tunnel | Electrical tunnel | A.218G. |  |  | Building volume | 1632 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 191674 | Fixed cost | 1 | 1
Non-essential switchgear building | Non-essential switchgear building | A.218H. |  |  | Building volume | 1800 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1628890 | Fixed cost | 1 | 1 | 393 |  | 30 | 50 | 3
Main steam and feedwater pipe | Substructure | A.218J.13 |  |  | Substructure volume | 504 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 3607517 | Fixed cost | 1 | 1 | 2400 |  | 380 |  | 20
Main steam and feedwater pipe | Superstructure concrete | A.218J.141 |  |  | Superstructure volume | 1771 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 19121421 | Fixed cost | 1 | 1 | 4500 |  | 990 |  | 150
Main steam and feedwater pipe | Structural & Misc steel | A.218J.142 |  |  | Building volume | 7560 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1619110 | Fixed cost | 1 | 1 |  |  |  | 50
Main steam and feedwater pipe | Roofing | A.218J.145 |  |  | Substructure area | 420 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 87209 | Fixed cost | 1 | 1
Main steam and feedwater pipe | Interior walls | A.218J.146 |  |  | Building volume | 7560 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 34472 | Fixed cost | 1 | 1
Main steam and feedwater pipe | Doors/windows | A.218J.147 |  |  | Building volume | 7560 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 20865 | Fixed cost | 1 | 1
Main steam and feedwater pipe | Painting | A.218J.149 |  |  | Superstructure area | 2952 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 125147 | Fixed cost | 1 | 1
Main steam and feedwater pipe | Plumbing & Drains | A.218J.21 |  |  | Building volume | 7560 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 1583164 | Fixed cost | 1 | 1
Main steam and feedwater pipe | HVAC | A.218J.22 |  |  | Plant power | 3417 | Structures - plant power costs | RX power | 3417 | Structures - plant power costs | Direct cost | 607654 | Fixed cost | 1 | 1 | [7 empty] | 4860
Main steam and feedwater pipe | Lighting & Service power | A.218J.24 |  |  | Building volume | 7560 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 667938 | Fixed cost | 1 | 1
Pipe tunnels | Pipe tunnels | A.218K. | [5 empty] | RX power | 3417 | Structures - plant power costs | Direct cost | 905841 | Fixed cost | 1 | 1 | 345 |  | 35 | 5 | 2
Technical support center | Technical support center | A.218L. | [5 empty] | RX power | 3417 | Structures - plant power costs | Direct cost | 2283038 | Fixed cost | 1 | 1 | 950 |  | 73 | 35
Containment hatch missile shield | Containment hatch missile shield | A.218P. |  |  | Building volume | 540 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 566431 | Fixed cost | 1 | 1 | 280 |  | 35
Waste water treatment building | Waste water treatment building | A.218S. |  |  | Building volume | 1152 | Structures - unit costs | RX power | 3417 | Structures - plant power costs | Direct cost | 2012135 | Fixed cost | 1 | 1 | 1220 |  | 62 | 15 | 1
Ultimate heat sink structure | Excavation | A.218T.11 |  |  | Building volume | 18630 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 1286877 | Fixed cost | 1 | 1
Ultimate heat sink structure | Substructure | A.218T.13 |  |  | Substructure volume | 972 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 926876 | Fixed cost | 1 | 1 | 1050 |  | 105 |  | 1
Ultimate heat sink structure | Superstructure concrete | A.218T.141 |  |  | Superstructure volume | 1904 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 10793613 | Fixed cost | 1 | 1 | 4400 |  | 510 |  | 10
Ultimate heat sink structure | Structural & Misc steel | A.218T.142 |  |  | Building volume | 18630 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 1264499 | Fixed cost | 1 | 1 |  |  |  | 110
Ultimate heat sink structure | Roofing | A.218T.145 |  |  | Substructure area | 810 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 85890 | Fixed cost | 1 | 1
Ultimate heat sink structure | Doors/windows | A.218T.147 |  |  | Building volume | 18630 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 9766 | Fixed cost | 1 | 1
Ultimate heat sink structure | Painting | A.218T.149 |  |  | Superstructure area | 3174 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 83831 | Fixed cost | 1 | 1
Ultimate heat sink structure | Plumbing & Drains | A.218T.21 |  |  | Building volume | 18630 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 44803 | Fixed cost | 1 | 1
Ultimate heat sink structure | HVAC | A.218T.22 |  |  | Plant power | 3417 | Structures - plant power costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 279196 | Fixed cost | 1 | 1
Ultimate heat sink structure | Lighting & Service power | A.218T.24 |  |  | Building volume | 18630 | Structures - unit costs | Plant power | 3417 | Structures - plant power costs | Direct cost | 346767 | Fixed cost | 1 | 1
Control room air intake structure | Control room air intake structure | A.218V. | [5 empty] | Plant power | 3417 | Structures - plant power costs | Direct cost | 240158 | Fixed cost | 1 | 1
Reactor equipment | RPV Structure + Support | A.221.1 | Vessel mass | [13128, 38, Pressure vessel - exponent, RPV - nuclear escalation] | Vessel mass | 387000 | Pressure vessel - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 75019941 | Fixed cost | 1 | 1
Reactor equipment | Control rods | A.221.2 |  |  | Number of CRs | 57 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 30753877 | Fixed cost | 1 | 1
Reactor equipment | RPV Internals | A.221.3 |  |  | Reactor diameter (m) | 4.6 | RPV internals - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 49698846 | Fixed cost | 1 | 1
Main heat transport system | Primary coolant pump | A.222.11 | Flow rate | [9054, 247, RCP - exponent, RCP - nuclear escalation] | Flow rate | 5430.88 | RCP - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 108401469 | Fixed cost | 1 | 1
Main heat transport system | Primary system piping | A.222.12 |  |  | MC piping mass | 154000 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 36197143 | Fixed cost | 1 | 1 | [7 empty] | 8990 | 151650
Main heat transport system | Steam generators | A.222.13 | HT surface area | [31688, 61, Heat exchanger - exponent, Steam generator - nuclear escalation] | HT surface area | 5126 | Heat exchanger - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 119461264 | Fixed cost | 1 | 1
Main heat transport system | Pressurizer | A.222.14 | Pressurizer mass | [13128, 38, Pressure vessel - exponent, Pressurizer - nuclear escalation] | Pressurizer mass | 91663 | Pressure vessel - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 8419993 | Fixed cost | 1 | 1
Safeguards system | Residual heat removal | A.223.1 | [5 empty] | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 17443131 | Fixed cost | 1 | 1 | [8 empty] | 60280
Safeguards system | Safety injection system | A.223.3 | [5 empty] | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 32329219 | Fixed cost | 1 | 1 | [7 empty] | 2150 | 62660
Safeguards system | Containment spray | A.223.4 |  |  | Containment volume | 92268 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 21141659 | Fixed cost | 1 | 1 | [7 empty] | 9930 | 120820
Safeguards system | Combustible gas control | A.223.5 |  |  | Containment volume | 92268 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 3366386 | Fixed cost | 1 | 1 | [7 empty] | 13400
Radwaste processing | Liquid waste system | A.224.1 |  |  | Primary flowrate | 23872 | Primary flow rate - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 43498466 | Fixed cost | 1 | 1 | [7 empty] | 296171 | 1738
Radwaste processing | Rad gas waste processing | A.224.2 |  |  | Primary flowrate | 23872 | Primary flow rate - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 4382355 | Fixed cost | 1 | 1 | [7 empty] | 7800
Radwaste processing | Solid waste system | A.224.3 | [5 empty] | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 20796213 | Fixed cost | 1 | 1 | [7 empty] | 24550
Fuel handling and storage | Fuel crane | A.225.111 | Fuel crane capacity | [411796, 3739, Crane - exponent, Crane - nuclear escalation] | Fuel crane capacity | 2 | Crane - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 391304 | Fixed cost | 1 | 1
Fuel handling and storage | Monorails/hoists | A.225.112 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 62594 | Fixed cost | 1 | 1
Fuel handling and storage | Fuel elevator | A.225.113 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 232257 | Fixed cost | 1 | 1
Fuel handling and storage | Spent fuel cask crane | A.225.114 | Fuel cask capacity | [411796, 3739, Crane - exponent, Crane - nuclear escalation] | Fuel cask capacity | 113 | Crane - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 1850028 | Fixed cost | 1 | 1
Fuel handling and storage | Fuel handling tools | A.225.12 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 355407 | Fixed cost | 1 | 1
Fuel handling and storage | Transfer system | A.225.13 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 1538750 | Fixed cost | 1 | 1
Fuel handling and storage | Service platforms | A.225.3 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 381137 | Fixed cost | 1 | 1
Fuel handling and storage | Fuel storage, cleaning, inspection | A.225.4 |  |  | SFP volume | 1056 | Fuel pool volume - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 6837991 | Fixed cost | 1 | 1 | [7 empty] | 11450 | 9150
Other reactor equipment | Intert gas system | A.226.1 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 4540150 | Fixed cost | 1 | 1 | [7 empty] | 47000
Other reactor equipment | Reactor makeup water system | A.226.3 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 5645240 | Fixed cost | 1 | 1 | [7 empty] | 49404 | 77
Other reactor equipment | Coolant treatment and recycle | A.226.4 |  |  | Primary flowrate | 23872 | Primary flow rate - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 64519555 | Fixed cost | 1 | 1 | [7 empty] | 102160 | 161600
Other reactor equipment | Fluid leak detection system | A.226.6 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 478670 | Fixed cost | 1 | 1
Other reactor equipment | Nuclear service water system | A.226.71 |  |  | RX power | 3417 | Reactor equipment - plant power costs | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 45445885 | Fixed cost | 1 | 1 | [8 empty] | 614600
Other reactor equipment | Primary component cooling water | A.226.72 |  |  | Primary flowrate | 23872 | Primary flow rate - exponent | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 31297550 | Fixed cost | 1 | 1 | [7 empty] | 165000 | 286730
Other reactor equipment | Maintenance equipment | A.226.8 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 10231040 | Fixed cost | 1 | 1
Other reactor equipment | Sampling equipment | A.226.9 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 2397864 | Fixed cost | 1 | 1 | [7 empty] | 3000
Reactor instrumentation and control | NSS Control Board | A.227.11 |  |  | Number of RXs | 1 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 3351758 | Fixed cost | 1 | 1
Reactor instrumentation and control | HVAC Panels | A.227.15 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 355599 | Fixed cost | 1 | 1
Reactor instrumentation and control | Radwaste Panels & Racks | A.227.16 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 1445229 | Fixed cost | 1 | 1
Reactor instrumentation and control | Local Panels & Cabinets | A.227.17 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 1408991 | Fixed cost | 1 | 1
Reactor instrumentation and control | Instrument Ranks | A.227.18 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 1476340 | Fixed cost | 1 | 1
Reactor instrumentation and control | Alarm System | A.227.19 |  |  | Number of CRs | 57 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 710824 | Fixed cost | 1 | 1
Reactor instrumentation and control | Process Computer | A.227.2 |  |  | Number of RXs | 1 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 7579214 | Fixed cost | 1 | 1
Reactor instrumentation and control | Monitoring Systems | A.227.3 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 9532951 | Fixed cost | 1 | 1
Reactor instrumentation and control | Plant Control Systems | A.227.4 |  |  | Number of CRs | 57 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 7571241 | Fixed cost | 1 | 1
Reactor instrumentation and control | Reactor Plant I&C Tubing & Fitting | A.227.5 |  |  | Number of CRs | 57 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 10234233 | Fixed cost | 1 | 1
Reactor instrumentation and control | TMI Instrumentation | A.227.9 |  |  | Number of CRs | 57 | 1 | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 8721364 | Fixed cost | 1 | 1
Reactor misc. equipment | Field Painting | A.228.1 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 2064008.504 | Fixed cost | 1 | 1
Reactor misc. equipment | Qualification of Welders | A.228.2 |  |  | Fixed cost |  |  | Plant power | 3417 | Reactor equipment - plant power costs | Direct cost | 8562632.532 | Fixed cost | 1 | 1
Reactor misc. equipment | Reactor Plant Insulation | A.228.4 |  |  | RPV insulated area | 250 | 1 | RX power | 3417 | Reactor equipment - plant power costs | Direct cost | 9736449.916 | Fixed cost | 1 | 1
NuScale Equipment | Containment vacuum pump | A.229.1 |  |  | Pump power (kW) | 100 | NuScale containment vacuum pump - exponent | RX power | 3417 | Reactor equipment - plant power costs | Direct cost | 730336.8307 | Fixed cost | 1 | 1
NuScale Equipment | Containment flooding & drain | A.229.2 |  |  | Evacuated volume (m3) | 40 | NuScale containment flooding drain - exponent | RX power | 3417 | Reactor equipment - plant power costs | Direct cost | 22978268 | Fixed cost | 1 | 1
HTGR Equipment | Reactor Cavity Cooling System | A.229.3 |  |  | RPV surface area (m2) | 150.7964 | HTGR RCCS - exponent | RX power | 230 | Reactor equipment - plant power costs | Direct cost | 17192142.03 | Fixed cost | 1 | 1
HTGR Equipment | Refueling Equipment | A.229.4 |  |  | Core diameter (m) | 4 | HTGR refueling - exponent | RX power | 230 | Reactor equipment - plant power costs | Direct cost | 34560408.78 | Fixed cost | 1 | 1
HTGR Equipment | He Purification Equipment | A.229.5 |  |  | He purif flow rate (kg/s) | 0.048133 | HTGR He purifcation - exponent | RX power | 12.55 | Reactor equipment - plant power costs | Direct cost | 3330589.647 | Fixed cost | 1 | 1
HTGR Equipment | He Circulator | A.229.6 | Circulator power (kW) | [580000, 20000, HTGR circulator - exponent, HTGR circulator - nuclear escalation] | Circulator power (kW) | 2791 | HTGR circulator - exponent | RX power | 230 | Reactor equipment - plant power costs | Direct cost | 6600420.207 | Fixed cost | 1 | 1
BWR | Isolation Condensers | A.229.7 |  |  | Thermal power | 854.25 | BWR isolation condenser - exponent | RX power | 3417 | Reactor equipment - plant power costs | Direct cost | 29711266 | Fixed cost | 1 | 1
Turbine plant equipment | Turbine Generator | A.231. | [5 empty] | Electric power | 1144 | Turbine equipment electric power - exponent | Direct cost | 303437900.3 | Fixed cost | 1 | 1 | 3700 |  | 440 | 5 | 45 |  |  | 187090
Turbine plant equipment | Condensing Systems | A.233. | [5 empty] | Electric power | 1144 | Turbine equipment electric power - exponent | Direct cost | 84792697.4 | Fixed cost | 1 | 1 | 650 |  | 65 |  | 2 |  |  | 1088500
Turbine plant equipment | Feedwater Heating System | A.234. |  |  | HT surface area | 79440.7713 | Heat exchanger - exponent | Electric power | 1144 | Turbine equipment electric power - exponent | Direct cost | 74747364.89 | Fixed cost | 1 | 1 | [7 empty] | 1138920 | 56940
Turbine plant equipment | Other Turbine Plant Equipment | A.235. | [5 empty] | Electric power | 1144 | Turbine equipment electric power - exponent | Direct cost | 91135906.37 | Fixed cost | 1 | 1 | 122 |  | 8 |  | 1 |  |  | 1330475 | 326000
Turbine plant equipment | Instrumentation & Control | A.236. | [5 empty] | Electric power | 1144 | Turbine equipment electric power - exponent | Direct cost | 17896323.63 | Fixed cost | 1 | 1
Turbine plant equipment | Turbine Plant Miscellaneous Items | A.237. | [5 empty] | Electric power | 1144 | Turbine equipment electric power - exponent | Direct cost | 21289794.43 | Fixed cost | 1 | 1
Electrical plant equipment | Switchgear | A.241. | [5 empty] | Electric power | 1144 | Electrical equipment electric power - exponent | Direct cost | 26306164 | Fixed cost | 1 | 1
Electrical plant equipment | Station Service Equipment | A.242. | [5 empty] | Electric power | 1144 | Electrical equipment electric power - exponent | Direct cost | 44768206 | Fixed cost | 1 | 1 | 440 |  | 30 |  | 2 |  |  |  | 705
Electrical plant equipment | Switchboards | A.243. | [5 empty] | Electric power | 1144 | Electrical equipment electric power - exponent | Direct cost | 4297174 | Fixed cost | 1 | 1
Electrical plant equipment | Protective Equipment | A.244. | [5 empty] | Electric power | 1144 | Electrical equipment electric power - exponent | Direct cost | 11073940 | Fixed cost | 1 | 1
Electrical plant equipment | Electrical Structure & Wiring Container | A.245. | [5 empty] | Electric power | 1144 | Electrical equipment electric power - exponent | Direct cost | 104279957 | Fixed cost | 1 | 1 | 5020 |  | 285
Electrical plant equipment | Power & Control Wiring | A.246. | [5 empty] | Electric power | 1144 | Electrical equipment electric power - exponent | Direct cost | 75382282 | Fixed cost | 1 | 1 | [6 empty] | 4978650
Transportation and lift equipment | TG Crane | A.251.111 | TG crane capacity | [411796, 3739, Crane - exponent, Crane - nuclear escalation] | TG crane capacity | 190 | Crane - exponent | RX power | 3417 | Misc. equipment - exponent | Direct cost | 3273323 | Fixed cost | 1 | 1
Transportation and lift equipment | HB crane | A.251.112 | Heater bay crane capacity | [411796, 3739, Crane - exponent, Crane - nuclear escalation] | Heater bay crane capacity | 90 | Crane - exponent | RX power | 3417 | Misc. equipment - exponent | Direct cost | 1317233 | Fixed cost | 1 | 1
Transportation and lift equipment | Containment crane | A.251.12 | Containment crane | [411796, 3739, Crane - exponent, Crane - nuclear escalation] | Containment crane | 380 | Crane - exponent | RX power | 3417 | Misc. equipment - exponent | Direct cost | 6941502 | Fixed cost | 1 | 1
Transportation and lift equipment | Misc. cranes | A.251.16 |  |  | Fixed cost | [5 empty] | Direct cost | 1303644 | Fixed cost | 1 | 1
Transportation and lift equipment | DG crane | A.251.17 | Diesel building crane | [411796, 3739, Crane - exponent, Crane - nuclear escalation] | Diesel building crane | 4.5 | Crane - exponent | RX power | 3417 | Misc. equipment - exponent | Direct cost | 1051195 | Fixed cost | 1 | 1
Air, water, and steam service system | Air system | A.252.1 |  |  | Volume of 212, 213, 215, 216, 217 | 416524 | Service system volume - exponent |  |  |  | Direct cost | 24444522 | Fixed cost | 1 | 1 | [7 empty] | 174800 | 68500
Air, water, and steam service system | Water system | A.252.2 |  |  | Volume of 212, 213, 215, 216, 217 | 416524 | Service system volume - exponent |  |  |  | Direct cost | 72411451 | Fixed cost | 1 | 1 | [7 empty] | 1196500
Air, water, and steam service system | Steam system | A.252.3 |  |  | Volume of 212, 213, 215, 216, 217 | 416524 | Service system volume - exponent |  |  |  | Direct cost | 15428628 | Fixed cost | 1 | 1 | [7 empty] | 279460
Air, water, and steam service system | Plant fuel oil system | A.252.4 |  |  | Fixed cost | [5 empty] | Direct cost | 755209 | Fixed cost | 1 | 1 | 30 |  | 5
Communications equipment | Communications equipment | A.253. |  |  | Volume of 212, 213, 215, 216, 217 | 416524 | Service system volume - exponent |  |  |  | Direct cost | 16185605 | Fixed cost | 1 | 1
Furnishings and fixtures | Furnishings and fixtures | A.254. |  |  | Volume of 212, 213, 215, 216, 217 | 416524 | Service system volume - exponent |  |  |  | Direct cost | 6467655 | Fixed cost | 1 | 1
Waste water treatment | Waste water treatment | A.255. |  |  | Fixed cost | [5 empty] | Direct cost | 6675261 | Fixed cost | 1 | 1
Heat rejection system | Makeup Water Intake Building | A.261.1 |  |  | Rejected thermal power | 2273 | Rejected thermal power - exponent | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 3187841 | Fixed cost | 1 | 1 | 700 |  | 55 | 27 | 15
Heat rejection system | Circulation Water Pump House | A.261.2 |  |  | Rejected thermal power | 2273 | Rejected thermal power - exponent | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 6628965 | Fixed cost | 1 | 1 | 2960 |  | 220 | 11 | 15 |  |  | 9120
Heat rejection system | Makeup Water Pretreatment Building | A.261.3 |  |  | Rejected thermal power | 2273 | Rejected thermal power - exponent | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 3622398 | Fixed cost | 1 | 1 | 852 |  | 59 | 130 | 2 |  |  | 10200
Heat Rejection System | Water Intake Equipment | A.262.11 |  |  | Rejected thermal power | 2273 | Rejected thermal power - exponent | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 1149076 | Fixed cost | 1 | 1 | [7 empty] | 1820
Heat Rejection System | Circulating Water System | A.262.12 |  |  | T/B Bldg - Cooling source distance (m) | 250 | 1 | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 37384462 | Fixed cost | 1 | 1 | 2350 |  | 44 |  |  |  |  | 708600
Heat Rejection System | Cooling Towers | A.262.13 |  |  | Rejected thermal power | 2273 | Rejected thermal power - exponent | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 75236688 | Fixed cost | 1 | 1
Heat Rejection System | Cooling Tower Basins | A.262.14 |  |  | Rejected thermal power | 2273 | Rejected thermal power - exponent | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 247554 | Fixed cost | 1 | 1
Heat Rejection System | Main Cooling Tower Makeup & Blowdown System | A.262.15 |  |  | Rejected thermal power | 2273 | Rejected thermal power - exponent | Plant power | 3417 | Heat rejection system - exponent | Direct cost | 3371679 | Fixed cost | 1 | 1 | [7 empty] | 820

## param_ranges
| Parameter | Base value | Distribution | Min value | Max value | mu/lambda | sigma | mean and/or median | Base ref | Min ref | Max ref | Min range | Max range
Modularization | Offsite work mult | 1 | lognormal | 0.5 | 1.25 | -0.235 | 0.23375 | 0.79057 | McKinsey | McKinsey | McKinsey | -50% | 25%
| Offsite efficiency mult | 1 | lognormal | 0.5 | 2 | 0 | 0.35365 | 1 | McKinsey | McKinsey | McKinsey | -50% | 100%
| Factory cost mult | 1 | lognormal | 0.85 | 1.2 | 0.0099013 | 0.087971 | 1.01 | Shaw Group |  |  | -15% | 20%
| Transportation cost factor | 1 | lognormal | 1.02 | 1.1 | 0.057556 | 0.019262 | 1.0592 | EMWG | McKinsey | McKinsey | 2% | 10%
Learning | Labor learning rate | 13.1% | lognormal | 4.679% | 23.39% | -2.2575 | 0.41058 | 0.10462 | EEDB, Lovering, Duffey | Lyons, Univ. Chicago | Lyons, Univ. Chicago | -64.29% | 78.57%
| Factory learning rate | 16% | lognormal | 5.714% | 28.57% | -2.0575 | 0.41058 | 0.12778 | EEDB, Lovering, Duffey | Lyons, Univ. Chicago | Lyons, Univ. Chicago | -64.29% | 78.57%
| Material learning rate | 7.1% | lognormal | 2.536% | 12.68% | -2.87 | 0.41058 | 0.0567 | EEDB, Lovering, Duffey | Lyons, Univ. Chicago | Lyons, Univ. Chicago | -64.29% | 78.57%
| Labor minimum | 55% | lognormal | 46.75% | 66% | -0.58794 | 0.087971 | 0.55547 | EEDB, Lovering, Duffey | + | + | -15% | 20%
| Material minimum | 73% | lognormal | 62.05% | 87.6% | -0.30481 | 0.087971 | 0.73726 | EEDB, Lovering, Duffey | + | + | -15% | 20%
Indirect cost scalars | [Indirect] Site Labor Cost | 0.36 | lognormal | 0.34 | 0.38 | -1.0232 | 0.028374 | 0.35944 | EEDB | EEDB | EEDB | -5.556% | 5.556%
| [Indirect] Site Labor Hours | 0.36 | lognormal | 0.34 | 0.38 | -1.0232 | 0.028374 | 0.35944 | EEDB | EEDB | EEDB | -5.556% | 5.556%
| [Indirect] Site Material Cost | 0.785 | lognormal | 0.72 | 0.86 | -0.23966 | 0.045328 | 0.78689 | EEDB | EEDB | EEDB | -8.28% | 9.554%
| [Indirect] Factory Equipment Cost | 3.661 | lognormal | 3.25 | 4.05 | 1.2887 | 0.056139 | 3.628 | EEDB | EEDB | EEDB | -11.23% | 10.63% | Could change to 1.32 and scale on direct labor
Design simplifications | [Simple] A.222.12: Reactor Coolant Piping | 0.25 | lognormal | 0.2125 | 0.3 | -1.3764 | 0.087971 | 0.25249 | EEDB | + | + | -15% | 20%
| [Simple] A.223: Safeguards system | 0.71 | lognormal | 0.6035 | 0.852 | -0.33259 | 0.087971 | 0.71706 | EEDB | + | + | -15% | 20%
| [Simple] A.224: Radwaste Processing | 0.76 | lognormal | 0.646 | 0.912 | -0.26454 | 0.087971 | 0.76756 | EEDB | + | + | -15% | 20%
| [Simple] A.225: Fuel Handling & Storage | 0.52 | lognormal | 0.442 | 0.624 | -0.64403 | 0.087971 | 0.52517 | EEDB | + | + | -15% | 20%
| [Simple] A.226: Other Reactor Equipment | 0.5 | lognormal | 0.425 | 0.6 | -0.68325 | 0.087971 | 0.50498 | EEDB | + | + | -15% | 20%
Passive safety | [Electrical] A.241: Switchgear | 0.54834 | lognormal | 0.46609 | 0.65801 | -0.59096 | 0.087971 | 0.5538 | EEDB | + | + | -15% | 20%
| [Electrical] A.242: Station Service Equipment | 0.26788 | lognormal | 0.2277 | 0.32146 | -1.3073 | 0.087971 | 0.27055 | EEDB | + | + | -15% | 20%
| [Electrical] A.243: Switchboards | 0.90623 | lognormal | 0.7703 | 1.0875 | -0.088556 | 0.087971 | 0.91525 | EEDB | + | + | -15% | 20%
| [Electrical] A.244: Protective Equipment | 1.0099 | lognormal | 0.85844 | 1.2119 | 0.019783 | 0.087971 | 1.02 | EEDB | + | + | -15% | 20%
| [Electrical] A.245: Electrical Structures & Wiring Containter | 0.57837 | lognormal | 0.49162 | 0.69404 | -0.53764 | 0.087971 | 0.58413 | EEDB | + | + | -15% | 20%
| [Electrical] A.246: Power & Control Wiring | 0.60509 | lognormal | 0.51433 | 0.72611 | -0.49248 | 0.087971 | 0.61111 | EEDB | + | + | -15% | 20%
Integral PWRs | 222.13 Steam generators reduction mult | 0.5 | lognormal | 0.425 | 0.6 | -0.68325 | 0.087971 | 0.50498 | EEDB | + | + | -15% | 20%
| 222.14 Pressurizer reduction mult | 0.1 | lognormal | 0.085 | 0.12 | -2.2927 | 0.087971 | 0.101 | EEDB | + | + | -15% | 20%
Steel plate composites | SPC steel cost escalation | 1.48 | lognormal | 1.258 | 1.776 | 0.40194 | 0.087971 | 1.4947 | Champlin | + | + | -15% | 20%
| SPC rebar reduction mult | 0% | exponential | 0% | 20% | 18.45 |  | 0.054201 | Champlin | + | + | 0% | 20%
| SPC operating engineer lift time (per 30 m2) | 8 | lognormal | 6.8 | 9.6 | 2.0893 | 0.087971 | 8.0796 | Champlin | + | + | -15% | 20%
| SPC weld time (per 30 m2) | 87 | lognormal | 73.95 | 104.4 | 4.4758 | 0.087971 | 87.8657 | Champlin | + | + | -15% | 20%
E-beam weld | E-beam weld cost reduction mult | 60% | lognormal | 60% | 80% | -0.36698 | 0.07339 | 0.69282 | EPRI | ? | ? | 0% | 33.33%
Standalone steel containment | 212.15 Factory cost mult | 3.25 | lognormal | 2.7625 | 3.9 | 1.1886 | 0.087971 | 3.2823 | EEDB | + | + | -15% | 20%
| 212.15 Labor hours mult | 4.86 | lognormal | 4.131 | 5.832 | 1.5909 | 0.087971 | 4.9084 | EEDB | + | + | -15% | 20%
| 212.15 Labor cost mult | 4.56 | lognormal | 3.876 | 5.472 | 1.5272 | 0.087971 | 4.6054 | EEDB | + | + | -15% | 20%
| 212.15 Material cost mult | 28.98 | lognormal | 24.633 | 34.776 | 3.3765 | 0.087971 | 29.2684 | EEDB | + | + | -15% | 20%
Cost scaling | Pool surface area cost | 17866 | uniform | 15186.1 | 21439.2 |  |  | 18312.65 | EEDB | + | + | -15% | 20%
| Structures - unit costs | 1 | uniform | 1 | 1 |  |  | 1 | Wibowo | ? | ? | 0% | 0%
| Structures - plant power costs | 0.8 | uniform | 0.588 | 0.8 |  |  | 0.694 | Saccheri | EEDB | EEDB | -26.5% | 0%
| Reactor equipment - plant power costs | 0.8 | uniform | 0.554 | 0.8 |  |  | 0.677 | Saccheri | EEDB | EEDB | -30.75% | 0%
| Pressure vessel - exponent | 0.85 | uniform | 0.65 | 0.85 |  |  | 0.75 | Towler | EMWG | Towler | -23.53% | 0%
| RPV - nuclear escalation | 34.4 | lognormal | 29.24 | 41.28 | 3.548 | 0.087971 | 34.7423 | EEDB, Ganda | + | + | -15% | 20%
| RPV internals - exponent | 2 | uniform | 1.8 | 2.2 |  |  | 2 | Towler | EMWG | Towler | -10% | 10%
| RCP - exponent | 0.92 | uniform | 0.41 | 0.92 |  |  | 0.665 | Towler | EMWG | Towler | -55.43% | 0%
| RCP - nuclear escalation | 39.7 | lognormal | 33.745 | 47.64 | 3.6913 | 0.087971 | 40.095 | EEDB, Ganda | + | + | -15% | 20%
| Heat exchanger - exponent | 1.2 | uniform | 0.65 | 1.2 |  |  | 0.925 | Towler | EMWG | Towler | -45.83% | 0%
| Steam generator - nuclear escalation | 17 | lognormal | 14.45 | 20.4 | 2.8431 | 0.087971 | 17.1692 | EEDB, Ganda | + | + | -15% | 20%
| Pressurizer - nuclear escalation | 12.98 | lognormal | 11.033 | 15.576 | 2.5733 | 0.087971 | 13.1092 | EEDB, Ganda | + | + | -15% | 20%
| Fuel pool volume - exponent | 0.75 | uniform | 0.71 | 0.79 |  |  | 0.75 | Towler | + | + | -5.333% | 5.333%
| Primary flow rate - exponent | 0.75 | uniform | 0.72 | 0.79 |  |  | 0.755 | Towler | + | + | -4% | 5.333%
| Crane - exponent | 1.26 | uniform | 1.22 | 1.3 |  |  | 1.26 | EEDB | + | + | -3.175% | 3.175%
| Crane - nuclear escalation | 1 | lognormal | 1 | 1 | 0 | 0 | 1 | EEDB | ? | ? | 0% | 0%
| NuScale containment vacuum pump - exponent | 0.6 | uniform | 0.41 | 0.6 |  |  | 0.505 | Towler | EMWG | Towler | -31.67% | 0%
| NuScale containment flooding drain - exponent | 0.85 | uniform | 0.81 | 0.89 |  |  | 0.85 | Towler | + | + | -4.706% | 4.706%
| HTGR RCCS - exponent | 1.21 | uniform | 1.17 | 1.25 |  |  | 1.21 | Gandrick | + | + | -3.306% | 3.306%
| HTGR refueling - exponent | 1.31 | uniform | 1.27 | 1.35 |  |  | 1.31 | Gandrick | + | + | -3.053% | 3.053%
| HTGR He purifcation - exponent | 0.6 | uniform | 0.56 | 0.64 |  |  | 0.6 | Towler | + | + | -6.667% | 6.667%
| HTGR circulator - exponent | 0.6 | uniform | 0.6 | 0.83 |  |  | 0.715 | Towler | Towler | EMWG | 0% | 38.33%
| HTGR circulator - nuclear escalation | 2.26 | lognormal | 1.921 | 2.712 | 0.82527 | 0.087971 | 2.2825 | EEDB | + | + | -15% | 20%
| BWR isolation condenser - exponent | 0.8 | uniform | 0.554 | 0.8 |  |  | 0.677 | Saccheri | EEDB | Saccheri | -30.75% | 0%
| Turbine equipment electric power - exponent | 0.8 | uniform | 0.6 | 0.834 |  |  | 0.717 | EEDB | Saccheri | EEDB | -25% | 4.25%
| Electrical equipment electric power - exponent | 0.6 | uniform | 0.487 | 0.6 |  |  | 0.5435 | Towler | EEDB | Towler | -18.83% | 0%
| Service system volume - exponent | 1 | uniform | 1 | 1 |  |  | 1 | ? | ? | ? | 0% | 0%
| Misc. equipment - exponent | 0.8 | uniform | 0.595 | 0.8 |  |  | 0.6975 | Saccheri | EEDB | Saccheri | -25.63% | 0%
| Rejected thermal power - exponent | 0.8 | uniform | 0.8 | 1.059 |  |  | 0.9295 | Saccheri | Saccheri | EEDB | 0% | 32.37%
| Heat rejection system - exponent | 0.8 | uniform | 0.8 | 1.059 |  |  | 0.9295 | Saccheri | Saccheri | EEDB | 0% | 32.37%
Material unit uncertainty | [Material] A.21: Structures & Improvements mult | 1 | lognormal | 0.85 | 1.15 | -0.011378 | 0.077114 | 0.98869 |  |  |  | -15% | 15%
| [Material] A.22: Reactor equipment mult | 1 | lognormal | 0.85 | 1.15 | -0.011378 | 0.077114 | 0.98869
| [Material] A.23: Turbine equipment mult | 1 | lognormal | 0.85 | 1.15 | -0.011378 | 0.077114 | 0.98869
| [Material] A.24: Electrical equipment mult | 1 | lognormal | 0.85 | 1.15 | -0.011378 | 0.077114 | 0.98869
| [Material] A.25: Misc plant equipment mult | 1 | lognormal | 0.85 | 1.15 | -0.011378 | 0.077114 | 0.98869
| [Material] A.26: Heat rejection system mult | 1 | lognormal | 0.85 | 1.15 | -0.011378 | 0.077114 | 0.98869
Note on E1: W. Robb Stewart: Min means the 0.025 quantile of the distribution if not normally distributed
Note on F1: W. Robb Stewart: Max means the 0.975 quantile of the distribution if not normally distributed
+ Indicates a forced -15%/+20% at 1/10 scale
? I have no idea